## Beckett Battery Modules
Boston Swing 5300 |  |  |  | Beckett 8224S Module |  |  |  | Approx |  | Stack of Beckett modules |  |  |  | Approx
| Nominal Capacity | 5.3 | Ah |  | Format Series | 7 | series |  |  |  | Format Series Stack | 11
| Nominal Energy | 19.3 | Wh |  | Format Parallel | 7 | parallel |  |  |  | Format Parallel Stack | 1
| Nominal Voltage | 3.65 | V |  | Nominal Capacity Module | 42.4 | Ah
| Max charge rate | 10.6 | A |  | Nominal Energy Module | 1100 | Wh
| Max discharge rate | 13 | A
| Voltage at 0% | 3.2 | V |  | Recommends 0.5C charge and 0.6C discharge
| Voltage at 30% | 3.4 | V
| Voltage at 80% | 3.85 | V
| Voltage at 100% | 4.2 | V |  | Voltage at 30% | 23.8 | V | 24V |  |  | Voltage at 30% | 261.8 | V | 260 | V | These are resting voltage numbers. When we're pushing
[5 empty] | Voltage at 80% | 26.95 | V | 27V |  |  | Voltage at 80% | 296.45 | V | 296 | V | charge into the stack, figure these numbers are going to be
around 10V higher.
[5 empty] | Checking module energy | 945.7 | Wh | 1kWh |  |  | Checking Stack Energy | 10402.7 | Wh | 10kWh
[5 empty] | Recommended charge 0.5C | 21.2 | A
[5 empty] | Recommended discharge 0.6C | 25 | A | 6950 | W
[5 empty] | Max discharge 1.2C | 50 | A
NovaTorque Alternator
| Rated load current | 24.4 | A
| Vac | 220 - 240 | Vac
| Vac peak 220 | 311.127 | Vac
| Vac peak 240 | 339.4113 | Vac
Looks like as the battery voltage comes up, the peaks of the sine waves
that make it through the rectifier get narrower. I bet this is the cause
of BK's observed drop of power into the battery.
This reminds me to look into the half wave / full wave rectifier question.

## Hygen Use Models
Info from Bill Kanz's 3 models of Hygen System Design, 3/1/2016.
Updates
| Beckett module nominal energy, kWh | 1 |  | Engine spec'd life, h | 20000
| Stack height | 11 |  | Hours in a year, h | 8760
| Batt bank energy, kWh | 11 |  | Engine service interval, h | 1000
| Batt end of life definition, capacity degradation | 80%
| Avg bank energy over lifetime | 90%
| Depth of Discharge, % | 63% |  |  |  | Our voltage limit switches are giving us about 16% to 79% SOC.
| Cycle energy, kWh | 6.237 |  | SFC, l/kWh | 0.38
| Batt Cycles 80% DOD | 3000 |  | Fuel Tank Capacity, l | 1000
| Batt Cycles 50% DOD, 0.5C charge, estimated by Boston Power | 10000 |  | Diesel cost, $/l | 1
| Bill Kanz's analysis: |  | 2 cylinder | 3 cylinder | 3 cylinder
|  |  |  | Limited by Engine Load Factor | Limited by Today's NovaTorque
A | Engine gross intermittent power, kW |  | 10.3 | 15.3 | 15.3
| Maximum engine load factor, % |  | 70% | 70% | 59%
B | Engine net intermittent power, kW |  | 7.21 | 10.71 | 9.027
| Engine efficiency (after fan, alternator, etc.), % |  | 88% | 88% | 88%
C | Engine max net weighted power, kW |  | 6.3448 | 9.4248 | 7.9438
| Alternator power efficiency, % |  | 94% | 94% | 94%
D | Alternator max output (calculated), kW |  | 5.9641 | 8.8593 | 7.4671
D | NovaTorque max power, kW |  | 7.5 | 8.8593 | 7.75 | We're actually running the NovaTorque above it spec.
| Rectifier power efficiency, % |  | 99% | 99% | 99%
E1 | Rectifier max output, kW |  | 5.9045 | 8.7707 | 7.6725
| DC - DC converter power efficiency, % |  | 95% | 95% | 93.8% | BK calculated this efficiency from our first 4kW Charge/Discharge cycle test.
F1 | Max rated DC power output, kW |  | 5.6092 | 8.3322 | 7.1968
F4 | Spec'd AC max accessory load, kW |  | 0.5 | 0.5 | 0.5
| Estimated AC inverter efficiency, % |  | 95% | 95% | 93.8%
F3 | AC accessory load, kW |  | 0.52632 | 0.52632 | 0.53305
F2 | Max rated tower load, kW |  | 5.0829 | 7.8059 | 6.6638
[7 empty] | Tower Load, kW | Fuel Cost per Month, $USD | 1000 liter tank refill interval, days | 250 liter tank refill interval, d | Engine maintenance interval, days | Fuel use per day, L
| Bill Marty's analysis: | [5 empty] | 0 | 0 |  |  |  | 0
| Working back upstream from tower load to battery charging. | Tower Load, kW |  |  |  |  | 0.5 | 139.08 | 219.2982 | 54.8246 | 589.264 | 4.56
E3 | Power available to charge battery bank, kW | 0 | 5.3505 | 8.2167 | 7.1042 |  | 1 | 278.16 | 109.6491 | 27.4123 | 293.255 | 9.12
| Power available to charge battery bank, kW | 0.5 | 4.8241 | 7.6904 | 6.5712 |  | 2 | 556.32 | 54.8246 | 13.7061 | 145.2504 | 18.24
| Power available to charge battery bank, kW | 1 | 4.2978 | 7.1641 | 6.0381 |  | 3 | 834.48 | 36.5497 | 9.1374 | 95.9156 | 27.36
| Power available to charge battery bank, kW | 2 | 3.2452 | 6.1114 | 4.972 |  | 4 | 1112.64 | 27.4123 | 6.8531 | 71.2482 | 36.48
| Power available to charge battery bank, kW | 3 | 2.1926 | 5.0588 | 3.9059 |  | 5 | 1390.8 | 21.9298 | 5.4825 | 56.4477 | 45.6
| Power available to charge battery bank, kW | 4 | 1.1399 | 4.0062 | 2.8398 |  | 6 | 1668.96 | 18.2749 | 4.5687 | 46.5808 | 54.72
| Power available to charge battery bank, kW | 5 | 0.087296 | 2.9535 | 1.7737
| Power available to charge battery bank, kW | 6 | -0.96534 | 1.9009 | 0.70763
| Battery C-rate w/ 0kW Tower Load |  | 0.54045 | 0.82997 | 0.7176
| Battery C-rate w/ 0.5kW Tower Load |  | 0.48729 | 0.77681 | 0.66375
| Battery C-rate w/ 1kW Tower Load |  | 0.43412 | 0.72364 | 0.60991
| Battery C-rate w/ 2kW Tower Load |  | 0.3278 | 0.61732 | 0.50222
| Battery C-rate w/ 3kW Tower Load |  | 0.22147 | 0.51099 | 0.39454
| Battery C-rate w/ 4kW Tower Load |  | 0.11514 | 0.40466 | 0.28685
| Battery C-rate w/ 5kW Tower Load |  | 0.0088178 | 0.29834 | 0.17916
| Battery C-rate w/ 6kW Tower Load |  | -0.097509 | 0.19201 | 0.071478
Tcharge | Engine on time to charge battery w/ 0kW Tower Load, h |  | 1.1657 | 0.75906 | 0.87793
| Engine on time to charge battery w/ 0.5kW Tower Load, h |  | 1.2929 | 0.81101 | 0.94915
| Engine on time to charge battery w/ 1kW Tower Load, h |  | 1.4512 | 0.87059 | 1.0329
| Engine on time to charge battery w/ 2kW Tower Load, h |  | 1.9219 | 1.0205 | 1.2544
| Engine on time to charge battery w/ 3kW Tower Load, h |  | 2.8446 | 1.2329 | 1.5968
| Engine on time to charge battery w/ 4kW Tower Load, h |  | 5.4714 | 1.5568 | 2.1963
| Engine on time to charge battery w/ 5kW Tower Load, h |  | 71.4463 | 2.1117 | 3.5163 | [7 empty] | These plots customized for Angus's Chilean customer.
| Engine on time to charge battery w/ 6kW Tower Load, h |  | -6.461 | 3.2811 | 8.8139
Tdischarge | Tower run time on battery w/ 0kW Tower Load, h | 0
| Tower run time on battery w/ 0.5kW Tower Load, h | 0.5 | 12.474 | 12.474 | 12.474
| Tower run time on battery w/ 1kW Tower Load, h | 1 | 6.237 | 6.237 | 6.237
| Tower run time on battery w/ 2kW Tower Load, h | 2 | 3.1185 | 3.1185 | 3.1185
| Tower run time on battery w/ 3kW Tower Load, h | 3 | 2.079 | 2.079 | 2.079
| Tower run time on battery w/ 4kW Tower Load, h | 4 | 1.5593 | 1.5593 | 1.5593
| Tower run time on battery w/ 5kW Tower Load, h | 5 | 1.2474 | 1.2474 | 1.2474
| Tower run time on battery w/ 6kW Tower Load, h | 6 | 1.0395 | 1.0395 | 1.0395
Tcycle | Cycle time w/ 0kW Tower Load, h
| Cycle time w/ 0.5kW Tower Load, h |  | 13.7669 | 13.285 | 13.4231
| Cycle time w/ 1kW Tower Load, h |  | 7.6882 | 7.1076 | 7.2699
| Cycle time w/ 2kW Tower Load, h |  | 5.0404 | 4.139 | 4.3729
| Cycle time w/ 3kW Tower Load, h |  | 4.9236 | 3.3119 | 3.6758
| Cycle time w/ 4kW Tower Load, h |  | 7.0306 | 3.1161 | 3.7555
| Cycle time w/ 5kW Tower Load, h |  | 72.6937 | 3.3591 | 4.7637
| Cycle time w/ 6kW Tower Load, h |  | -5.4215 | 4.3206 | 9.8534
Engine duty cycle w/ 0kW Tower Load, %
| Engine duty cycle w/ 0.5kW Tower Load, % |  | 0.093912 | 0.061047 | 0.07071
| Engine duty cycle w/ 1kW Tower Load, % |  | 0.18876 | 0.12249 | 0.14208
| Engine duty cycle w/ 2kW Tower Load, % |  | 0.3813 | 0.24657 | 0.28686
| Engine duty cycle w/ 3kW Tower Load, % |  | 0.57775 | 0.37226 | 0.43441
| Engine duty cycle w/ 4kW Tower Load, % |  | 0.77822 | 0.49961 | 0.58481
| Engine duty cycle w/ 5kW Tower Load, % |  | 0.98284 | 0.62865 | 0.73815
| Engine duty cycle w/ 6kW Tower Load, % |  | Error | 0.75941 | 0.8945
| Engine life in years w/ 0kW Tower Load, y | 0
| Engine life in years w/ 0.5kW Tower Load, y | 0.5 | 24.3111 | 37.399 | 32.2884
| Engine life in years w/ 1kW Tower Load, y | 1 | 12.0955 | 18.6394 | 16.0688
| Engine life in years w/ 2kW Tower Load, y | 2 | 5.9877 | 9.2596 | 7.9589
| Engine life in years w/ 3kW Tower Load, y | 3 | 3.9517 | 6.133 | 5.2556
| Engine life in years w/ 4kW Tower Load, y | 4 | 2.9337 | 4.5697 | 3.904
| Engine life in years w/ 5kW Tower Load, y | 5 | 2.323 | 3.6318 | 3.093
| Engine life in years w/ 6kW Tower Load, y | 6 | Error | 3.0064 | 2.5524
| Battery life in years w/ 0kW Tower Load, y | 0
| Battery life in years w/ 0.5kW Tower Load, y | 0.5 | 15.7156 | 15.1655 | 15.3232
| Battery life in years w/ 1kW Tower Load, y | 1 | 8.7765 | 8.1137 | 8.299
| Battery life in years w/ 2kW Tower Load, y | 2 | 5.7539 | 4.7249 | 4.9919
| Battery life in years w/ 3kW Tower Load, y | 3 | 5.6206 | 3.7807 | 4.1961
| Battery life in years w/ 4kW Tower Load, y | 4 | 8.0259 | 3.5572 | 4.2871
| Battery life in years w/ 5kW Tower Load, y | 5 | 82.9836 | 3.8346 | 5.438
| Battery life in years w/ 6kW Tower Load, y | 6 | Error | 4.9321 | 11.2482
| Engine maintenance interval w/ 0kW T.L., d | 0
| Engine maintenance interval w/ 0.5kW T.L., d | 0.5 | 443.6782 | 682.5322 | 589.264
| Engine maintenance interval w/ 1kW T.L., d | 1 | 220.7426 | 340.1696 | 293.255
| Engine maintenance interval w/ 2kW T.L., d | 2 | 109.2748 | 168.9883 | 145.2504
| Engine maintenance interval w/ 3kW T.L., d | 3 | 72.1189 | 111.9279 | 95.9156
| Engine maintenance interval w/ 4kW T.L., d | 4 | 53.5409 | 83.3977 | 71.2482
| Engine maintenance interval w/ 5kW T.L., d | 5 | 42.3941 | 66.2795 | 56.4477
| Engine maintenance interval w/ 6kW T.L., d | 6 | Error | 54.8674 | 46.5808

## 5 year life projections
Info from Bill Kanz's 3 models of Hygen System Design, 3/1/2016.
| Battery Parameters |  |  | Battery Parameters |  |  | 4 sets of assumptions
| Beckett module nominal energy, kWh | 1 |  | Beckett module nominal energy, kWh | 1 | 1 | 1 | 1.1
| Stack height | 11 |  | Stack height | 11 | 11 | 11 | 11
| Batt bank energy, kWh | 11 |  | Batt bank energy, kWh | 11 | 11 | 11 | 12.1
| Batt end of life definition, capacity degradation | 80% |  | Batt end of life definition, capacity degradation | 80% | 80% | 80% | 70%
| Avg bank energy over lifetime | 90% |  | Avg bank energy over lifetime | 90% | 90% | 90% | 85%
| Depth of Discharge, % | 50% |  | Depth of Discharge, % | 80% | 50% | 50% | 50%
| Cycle energy, kWh | 4.95 |  | Cycle energy, kWh | 7.92 | 4.95 | 4.95 | 5.1425
| Batt Cycles 80% DOD | 3000 |  | Batt Cycles 80% DOD | 3000 | 3000 | 3000 | 3000
| Batt Cycles 50% DOD, 0.5C charge, estimated by Boston Power | 10000 |  | Batt Cycles 50% DOD, 0.5C charge, estimated by Boston Power | 7500 | 7500 | 10000 | 10000
| Batt Cycles, projected based on end of life extension |  |  | Batt Cycles, projected based on end of life extension | 3000 | 7500 | 10000 | 15000
| Engine Parameters |  |  | Engine Parameters
| Engine spec'd life, h | 20000 |  | Engine spec'd life, h | 15000 | 15000 | 20000 | 25000
| Hours in a year, h | 8760 |  | Hours in a year, h | 8760 | 8760 | 8760 | 8760
| Engine service interval, h | 1000 |  | Engine service interval, h | 1000 | 1000 | 1000 | 1000
| SFC, l/kWh | 0.38 |  | SFC, l/kWh | 0.38 | 0.38 | 0.38 | 0.38
| Fuel Tank Capacity, l | 1000 |  | Fuel Tank Capacity, l | 1000 | 1000 | 1000 | 1000
| Diesel cost, $/l | 1 |  | Diesel cost, $/l | 1 | 1 | 1 | 1
| Bill Kanz's analysis: |  | 3 cylinder
Limited by Today's NovaTorque
A | Engine gross intermittent power, kW |  | 15.3
| Maximum engine load factor, % |  | 59%
B | Engine net intermittent power, kW |  | 9.027
| Engine efficiency (after fan, alternator, etc.), % |  | 88%
C | Engine max net weighted power, kW |  | 7.9438
| Alternator power efficiency, % |  | 94%
D | Alternator max output (calculated), kW |  | 7.4671
D | NovaTorque max power, kW |  | 7.5
| Rectifier power efficiency, % |  | 99%
E1 | Rectifier max output, kW |  | 7.425
| DC - DC converter power efficiency, % |  | 95%
F1 | Max rated DC power output, kW |  | 7.0537
F4 | Spec'd AC max accessory load, kW |  | 0
| Estimated AC inverter efficiency, % |  | 95%
F3 | AC accessory load, kW |  | 0
F2 | Max rated tower load, kW |  | 7.0537
[9 empty] | Tower Load, kW | Fuel Cost per Month, $USD | 1000 liter tank refill interval, days | 250 liter tank refill interval, d | Engine maintenance interval, days
| Bill Marty's analysis: |  |  |  | Beckett battery spec | Life under most conservative assumptions | Middle case | Life under most optimistic assumptions | 0 | 0
| Working back upstream from tower load to battery charging. | Tower Load, kW | [6 empty] | 0.5 | 139.08 | 219.2982 | 54.8246 | 616.557
E3 | Power available to charge battery bank, kW | 0 | 7.425 |  | 7.425 | 7.425 | 7.425 | 7.425 | 1 | 278.16 | 109.6491 | 27.4123 | 307.182
| Power available to charge battery bank, kW | 0.5 | 6.8987 |  | 6.8987 | 6.8987 | 6.8987 | 6.8987 | 2 | 556.32 | 54.8246 | 13.7061 | 152.4945
| Power available to charge battery bank, kW | 1 | 6.3724 |  | 6.3724 | 6.3724 | 6.3724 | 6.3724 | 3 | 834.48 | 36.5497 | 9.1374 | 100.932
| Power available to charge battery bank, kW | 2 | 5.3197 |  | 5.3197 | 5.3197 | 5.3197 | 5.3197 | 4 | 1112.64 | 27.4123 | 6.8531 | 75.1508
| Power available to charge battery bank, kW | 3 | 4.2671 |  | 4.2671 | 4.2671 | 4.2671 | 4.2671 | 5 | 1390.8 | 21.9298 | 5.4825 | 59.682
| Power available to charge battery bank, kW | 4 | 3.2145 |  | 3.2145 | 3.2145 | 3.2145 | 3.2145 | 6 | 1668.96 | 18.2749 | 4.5687 | 49.3695
| Power available to charge battery bank, kW | 5 | 2.1618 |  | 2.1618 | 2.1618 | 2.1618 | 2.1618
| Power available to charge battery bank, kW | 6 | 1.1092 |  | 1.1092 | 1.1092 | 1.1092 | 1.1092
| Battery C-rate w/ 0kW Tower Load |  | 0.75 |  | 0.75 | 0.75 | 0.75 | 0.72193
| Battery C-rate w/ 0.5kW Tower Load |  | 0.69684 |  | 0.69684 | 0.69684 | 0.69684 | 0.67075
| Battery C-rate w/ 1kW Tower Load |  | 0.64367 |  | 0.64367 | 0.64367 | 0.64367 | 0.61958
| Battery C-rate w/ 2kW Tower Load |  | 0.53735 |  | 0.53735 | 0.53735 | 0.53735 | 0.51723
| Battery C-rate w/ 3kW Tower Load |  | 0.43102 |  | 0.43102 | 0.43102 | 0.43102 | 0.41489
| Battery C-rate w/ 4kW Tower Load |  | 0.32469 |  | 0.32469 | 0.32469 | 0.32469 | 0.31254
| Battery C-rate w/ 5kW Tower Load |  | 0.21837 |  | 0.21837 | 0.21837 | 0.21837 | 0.21019
| Battery C-rate w/ 6kW Tower Load |  | 0.11204 |  | 0.11204 | 0.11204 | 0.11204 | 0.10785
Tcharge | Engine on time to charge battery w/ 0kW Tower Load, h |  | 0.66667 |  | 1.0667 | 0.66667 | 0.66667 | 0.69259
| Engine on time to charge battery w/ 0.5kW Tower Load, h |  | 0.71753 |  | 1.148 | 0.71753 | 0.71753 | 0.74543
| Engine on time to charge battery w/ 1kW Tower Load, h |  | 0.77679 |  | 1.2429 | 0.77679 | 0.77679 | 0.807
| Engine on time to charge battery w/ 2kW Tower Load, h |  | 0.9305 |  | 1.4888 | 0.9305 | 0.9305 | 0.96668
| Engine on time to charge battery w/ 3kW Tower Load, h |  | 1.16 |  | 1.8561 | 1.16 | 1.16 | 1.2051
| Engine on time to charge battery w/ 4kW Tower Load, h |  | 1.5399 |  | 2.4639 | 1.5399 | 1.5399 | 1.5998
| Engine on time to charge battery w/ 5kW Tower Load, h |  | 2.2897 |  | 3.6635 | 2.2897 | 2.2897 | 2.3788 | [5 empty] | These plots customized for Angus's Chilean customer.
| Engine on time to charge battery w/ 6kW Tower Load, h |  | 4.4626 |  | 7.1402 | 4.4626 | 4.4626 | 4.6362
Tdischarge | Tower run time on battery w/ 0kW Tower Load, h | 0
| Tower run time on battery w/ 0.5kW Tower Load, h | 0.5 | 9.9 |  | 15.84 | 9.9 | 9.9 | 10.285
| Tower run time on battery w/ 1kW Tower Load, h | 1 | 4.95 |  | 7.92 | 4.95 | 4.95 | 5.1425
| Tower run time on battery w/ 2kW Tower Load, h | 2 | 2.475 |  | 3.96 | 2.475 | 2.475 | 2.5713
| Tower run time on battery w/ 3kW Tower Load, h | 3 | 1.65 |  | 2.64 | 1.65 | 1.65 | 1.7142
| Tower run time on battery w/ 4kW Tower Load, h | 4 | 1.2375 |  | 1.98 | 1.2375 | 1.2375 | 1.2856
| Tower run time on battery w/ 5kW Tower Load, h | 5 | 0.99 |  | 1.584 | 0.99 | 0.99 | 1.0285
| Tower run time on battery w/ 6kW Tower Load, h | 6 | 0.825 |  | 1.32 | 0.825 | 0.825 | 0.85708
Tcycle | Cycle time w/ 0kW Tower Load, h
| Cycle time w/ 0.5kW Tower Load, h |  | 10.6175 |  | 16.988 | 10.6175 | 10.6175 | 11.0304
| Cycle time w/ 1kW Tower Load, h |  | 5.7268 |  | 9.1629 | 5.7268 | 5.7268 | 5.9495
| Cycle time w/ 2kW Tower Load, h |  | 3.4055 |  | 5.4488 | 3.4055 | 3.4055 | 3.5379
| Cycle time w/ 3kW Tower Load, h |  | 2.81 |  | 4.4961 | 2.81 | 2.81 | 2.9193
| Cycle time w/ 4kW Tower Load, h |  | 2.7774 |  | 4.4439 | 2.7774 | 2.7774 | 2.8854
| Cycle time w/ 5kW Tower Load, h |  | 3.2797 |  | 5.2475 | 3.2797 | 3.2797 | 3.4073
| Cycle time w/ 6kW Tower Load, h |  | 5.2876 |  | 8.4602 | 5.2876 | 5.2876 | 5.4933
Engine duty cycle w/ 0kW Tower Load, %
| Engine duty cycle w/ 0.5kW Tower Load, % |  | 0.06758 |  | 0.06758 | 0.06758 | 0.06758 | 0.06758
| Engine duty cycle w/ 1kW Tower Load, % |  | 0.13564 |  | 0.13564 | 0.13564 | 0.13564 | 0.13564
| Engine duty cycle w/ 2kW Tower Load, % |  | 0.27323 |  | 0.27323 | 0.27323 | 0.27323 | 0.27323
| Engine duty cycle w/ 3kW Tower Load, % |  | 0.41282 |  | 0.41282 | 0.41282 | 0.41282 | 0.41282
| Engine duty cycle w/ 4kW Tower Load, % |  | 0.55444 |  | 0.55444 | 0.55444 | 0.55444 | 0.55444
| Engine duty cycle w/ 5kW Tower Load, % |  | 0.69814 |  | 0.69814 | 0.69814 | 0.69814 | 0.69814
| Engine duty cycle w/ 6kW Tower Load, % |  | 0.84398 |  | 0.84398 | 0.84398 | 0.84398 | 0.84398
| Engine life in years w/ 0kW Tower Load, y | 0
| Engine life in years w/ 0.5kW Tower Load, y | 0.5 | 33.7839 |  | 25.338 | 25.338 | 33.7839 | 42.2299
| Engine life in years w/ 1kW Tower Load, y | 1 | 16.8319 |  | 12.6239 | 12.6239 | 16.8319 | 21.0399
| Engine life in years w/ 2kW Tower Load, y | 2 | 8.3559 |  | 6.2669 | 6.2669 | 8.3559 | 10.4448
| Engine life in years w/ 3kW Tower Load, y | 3 | 5.5305 |  | 4.1479 | 4.1479 | 5.5305 | 6.9132
| Engine life in years w/ 4kW Tower Load, y | 4 | 4.1179 |  | 3.0884 | 3.0884 | 4.1179 | 5.1473
| Engine life in years w/ 5kW Tower Load, y | 5 | 3.2702 |  | 2.4527 | 2.4527 | 3.2702 | 4.0878
| Engine life in years w/ 6kW Tower Load, y | 6 | 2.7052 |  | 2.0289 | 2.0289 | 2.7052 | 3.3815
| Battery life in years w/ 0kW Tower Load, y | 0
| Battery life in years w/ 0.5kW Tower Load, y | 0.5 | 12.1205 |  | 5.8178 | 9.0903 | 12.1205 | 18.8877
| Battery life in years w/ 1kW Tower Load, y | 1 | 6.5374 |  | 3.138 | 4.9031 | 6.5374 | 10.1875
| Battery life in years w/ 2kW Tower Load, y | 2 | 3.8876 |  | 1.866 | 2.9157 | 3.8876 | 6.0581
| Battery life in years w/ 3kW Tower Load, y | 3 | 3.2078 |  | 1.5397 | 2.4059 | 3.2078 | 4.9988
| Battery life in years w/ 4kW Tower Load, y | 4 | 3.1706 |  | 1.5219 | 2.3779 | 3.1706 | 4.9408
| Battery life in years w/ 5kW Tower Load, y | 5 | 3.744 |  | 1.7971 | 2.808 | 3.744 | 5.8343
| Battery life in years w/ 6kW Tower Load, y | 6 | 6.0361 |  | 2.8973 | 4.5271 | 6.0361 | 9.4063
| Engine maintenance interval w/ 0kW T.L., d | 0
| Engine maintenance interval w/ 0.5kW T.L., d | 0.5 | 616.557 |  | 616.557 | 616.557 | 616.557 | 616.557
| Engine maintenance interval w/ 1kW T.L., d | 1 | 307.182 |  | 307.182 | 307.182 | 307.182 | 307.182
| Engine maintenance interval w/ 2kW T.L., d | 2 | 152.4945 |  | 152.4945 | 152.4945 | 152.4945 | 152.4945
| Engine maintenance interval w/ 3kW T.L., d | 3 | 100.932 |  | 100.932 | 100.932 | 100.932 | 100.932
| Engine maintenance interval w/ 4kW T.L., d | 4 | 75.1508 |  | 75.1508 | 75.1508 | 75.1508 | 75.1508
| Engine maintenance interval w/ 5kW T.L., d | 5 | 59.682 |  | 59.682 | 59.682 | 59.682 | 59.682
| Engine maintenance interval w/ 6kW T.L., d | 6 | 49.3695 |  | 49.3695 | 49.3695 | 49.3695 | 49.3695

## Boston Power Life
2016-05-12 | Estimating points on the pink curve above to use in extrapolating our battery life.
| Cycle | BP Published Graph | BP 50% DOD Projected | Cycle | PPI 70% EOL | Cycle | PPI 50% DOD guestimate | Cycle | Beckett Spec
| 0 | 100 | 100 | 0 | 100 | 0 | 100 | 3000 | 80
| 500 | 92.1 | 92.1 | 500 | 92.1 | 1000 | 88.9
| 1000 | 88.9 | 88.9 | 1000 | 88.9 | 7500 | 80
| 1500 | 87.3 | 87.3 | 1500 | 87.3
| 2000 | 86.1 | 86.1 | 2000 | 86.1
| 2500 | 85.3 | 85.3 | 2500 | 85.3
| 3000 | 84.5 | 84.5 | 3000 | 84.5
| 3500 | 84.1 | 84.1 | 3500 | 84.1
| 10000 |  | 80 | 15000 | 70

## LTO comparison
2016-09-30
Toshiba LTO Design
Exists?
|  | Beckett 8224S | Toshiba SCiB 2P12S | Ratio | Toshiba SCiB 1P12S
| Voltage, nominal | 24 | 27.6 |  | 27.6
| Voltage, operating max | 28.7 | 32.4 |  | 32.4
| Voltage, operating min | 21 | 18 |  | 18
| Nominal capacity, Ah, 100% DOD | 42.4 | 40 |  | 20
| Dimensions, mm | 600 | 359 |  | 359
| Dimensions, mm | 210 | 187 |  | 93.5
| Dimensions, mm | 56 | 123 |  | 123
| Weight, kg | 8 | 14 |  | 7
| Max charge rate, A | 21.2 | 120 |  | 120
| Cycle life, 80% DOD | 3000 | 15000 |  | 15000
| Est cycle life, 50% DOD | 10000
| Stack height, modules | 11 | 10 |  | 10
| Charge peak voltage | 308 | 324 |  | 324
| Discharge minimum voltage | 262 | 180 |  | 180
| Enatel minimum voltage range | 200 | 360 |  | 360
| Vicor minimum voltage range | 180 | 375 |  | 375
| Nominal total energy/module, Wh | 1017.6 | 1104 |  | 552
| Nominal total energy/stack, Wh | 11193.6 | 11040 |  | 5520
| Designed DoD, fraction | 0.55 | 0.8 |  | 0.8
| Cycle energy, Wh | 6156.48 | 8832 |  | 4416 | 0.71729
| Lifetime energy delivered, kWh | 55408.32 | 119232 | 2.1519 | 59616 | 1.0759
| stack mass, kg | 88 | 140 | 1.5909 | 70 | 0.79545
| stack volume, m^3 | 0.077616 | 0.082574 | 1.0639 | 0.041287 | 0.53194