## Beckett Battery Modules
Boston Swing 5300 |  |  |  | Beckett 8224S Module |  |  |  | Approx |  | Stack of Beckett modules |  |  |  | Approx
| Nominal Capacity | 5.3 | Ah |  | Format Series | 7 | series |  |  |  | Format Series Stack | 11
| Nominal Energy | 19.3 | Wh |  | Format Parallel | 7 | parallel |  |  |  | Format Parallel Stack | 1
| Nominal Voltage | 3.65 | V |  | Nominal Capacity Module | 42.4 | Ah
| Max charge rate | 10.6 | A |  | Nominal Energy Module | 1100 | Wh
| Max discharge rate | 13 | A
| Voltage at 0% | 3.2 | V |  | Recommends 0.5C charge and 0.6C discharge
| Voltage at 30% | 3.4 | V
| Voltage at 80% | 3.85 | V
| Voltage at 100% | 4.2 | V |  | Voltage at 30% | 23.8 | V | 24V |  |  | Voltage at 30% | 261.8 | V | 260 | V | These are resting voltage numbers. When we're pushing
[5 empty] | Voltage at 80% | 26.95 | V | 27V |  |  | Voltage at 80% | 296.45 | V | 296 | V | charge into the stack, figure these numbers are going to be
around 10V higher.
[5 empty] | Checking module energy | 945.7 | Wh | 1kWh |  |  | Checking Stack Energy | 10402.7 | Wh | 10kWh
[5 empty] | Recommended charge 0.5C | 21.2 | A
[5 empty] | Recommended discharge 0.6C | 25 | A | 6950 | W
[5 empty] | Max discharge 1.2C | 50 | A
NovaTorque Alternator
| Rated load current | 24.4 | A
| Vac | 220 - 240 | Vac
| Vac peak 220 | 311.127 | Vac
| Vac peak 240 | 339.4113 | Vac
Looks like as the battery voltage comes up, the peaks of the sine waves
that make it through the rectifier get narrower. I bet this is the cause
of BK's observed drop of power into the battery.
This reminds me to look into the half wave / full wave rectifier question.

## Hygen Use Models
Info from Bill Kanz's 3 models of Hygen System Design, 3/1/2016.
| Beckett module nominal energy, kWh | 1 |  | Engine spec'd life, h | 15000
| Stack height | 11 |  | Hours in a year, h | 8760
| Batt bank energy, kWh | 11 |  | Engine service interval, h | 1000
| Depth of Discharge, % | 50%
| Cycle energy, kWh | 5.5 |  | SFC, l/kWh | 0.38
| Batt Cycles 80% DOD | 3000 |  | Fuel Tank Capacity, l | 1000
| Batt Cycles 50% DOD, estimated. | 7500 |  | Diesel cost, $/l | 1
| Bill Kanz's analysis: |  | 2 cylinder | 3 cylinder | 3 cylinder
|  |  |  | Limited by Engine Load Factor | Limited by Today's NovaTorque
A | Engine gross intermittent power, kW |  | 10.3 | 15.3 | 15.3
| Maximum engine load factor, % |  | 70% | 70% | 59%
B | Engine net intermittent power, kW |  | 7.21 | 10.71 | 9.027
| Engine efficiency (after fan, alternator, etc.), % |  | 88% | 88% | 88%
C | Engine max net weighted power, kW |  | 6.3448 | 9.4248 | 7.9438
| Alternator power efficiency, % |  | 94% | 94% | 94%
D | Alternator max output (calculated), kW |  | 5.9641 | 8.8593 | 7.4671
D | NovaTorque max power, kW |  | 7.5 | 8.8593 | 7.5
| Rectifier power efficiency, % |  | 99% | 99% | 99%
E1 | Rectifier max output, kW |  | 5.9045 | 8.7707 | 7.425
| DC - DC converter power efficiency, % |  | 95% | 95% | 95%
F1 | Max rated DC power output, kW |  | 5.6092 | 8.3322 | 7.0537
F4 | Spec'd AC max accessory load, kW |  | 0.5 | 0.5 | 0.5
| Estimated AC inverter efficiency, % |  | 95% | 95% | 95%
F3 | AC accessory load, kW |  | 0.52632 | 0.52632 | 0.52632
F2 | Max rated tower load, kW |  | 5.0829 | 7.8059 | 6.5274
Bill Marty's analysis:
| Working back upstream from tower load to battery charging. | Tower Load, kW |  |  |  | Tower Load, kW | Fuel Cost per Month, $USD | 1000 liter tank refill interval, days | 250 liter tank refill interval, d | Engine maintenance interval, days
E3 | Power available to charge battery bank, kW | 0 | 5.3505 | 8.2167 | 6.871 | 0 | 0
| Power available to charge battery bank, kW | 0.5 | 4.8241 | 7.6904 | 6.3447 | 0.5 | 139.08 | 219.2982 | 54.8246 | 570.389
| Power available to charge battery bank, kW | 1 | 4.2978 | 7.1641 | 5.8184 | 1 | 278.16 | 109.6491 | 27.4123 | 284.098
| Power available to charge battery bank, kW | 2 | 3.2452 | 6.1114 | 4.7657 | 2 | 556.32 | 54.8246 | 13.7061 | 140.9525
| Power available to charge battery bank, kW | 3 | 2.1926 | 5.0588 | 3.7131 | 3 | 834.48 | 36.5497 | 9.1374 | 93.2373
| Power available to charge battery bank, kW | 4 | 1.1399 | 4.0062 | 2.6605 | 4 | 1112.64 | 27.4123 | 6.8531 | 69.3798
| Power available to charge battery bank, kW | 5 | 0.087296 | 2.9535 | 1.6078 | 5 | 1390.8 | 21.9298 | 5.4825 | 55.0652
| Power available to charge battery bank, kW | 6 | -0.96534 | 1.9009 | 0.55519 | 6 | 1668.96 | 18.2749 | 4.5687 | 45.5222
| Battery C-rate w/ 0kW Tower Load |  | 0.4864 | 0.74697 | 0.62463
| Battery C-rate w/ 0.5kW Tower Load |  | 0.43856 | 0.69913 | 0.57679
| Battery C-rate w/ 1kW Tower Load |  | 0.39071 | 0.65128 | 0.52894
| Battery C-rate w/ 2kW Tower Load |  | 0.29502 | 0.55559 | 0.43325
| Battery C-rate w/ 3kW Tower Load |  | 0.19932 | 0.45989 | 0.33755
| Battery C-rate w/ 4kW Tower Load |  | 0.10363 | 0.3642 | 0.24186
| Battery C-rate w/ 5kW Tower Load |  | 0.007936 | 0.2685 | 0.14617
| Battery C-rate w/ 6kW Tower Load |  | -0.087758 | 0.17281 | 0.050472
Tcharge | Engine on time to charge battery w/ 0kW Tower Load, h |  | 1.028 | 0.66937 | 0.80047
| Engine on time to charge battery w/ 0.5kW Tower Load, h |  | 1.1401 | 0.71518 | 0.86687
| Engine on time to charge battery w/ 1kW Tower Load, h |  | 1.2797 | 0.76772 | 0.94528
| Engine on time to charge battery w/ 2kW Tower Load, h |  | 1.6948 | 0.89995 | 1.1541
| Engine on time to charge battery w/ 3kW Tower Load, h |  | 2.5085 | 1.0872 | 1.4812
| Engine on time to charge battery w/ 4kW Tower Load, h |  | 4.8249 | 1.3729 | 2.0673
| Engine on time to charge battery w/ 5kW Tower Load, h |  | 63.0038 | 1.8622 | 3.4208
| Engine on time to charge battery w/ 6kW Tower Load, h |  | -5.6975 | 2.8933 | 9.9064
These plots customized for Angus's Chilean customer.
Tdischarge | Tower run time on battery w/ 0kW Tower Load, h | 0
| Tower run time on battery w/ 0.5kW Tower Load, h | 0.5 | 11 | 11 | 11
| Tower run time on battery w/ 1kW Tower Load, h | 1 | 5.5 | 5.5 | 5.5
| Tower run time on battery w/ 2kW Tower Load, h | 2 | 2.75 | 2.75 | 2.75
| Tower run time on battery w/ 3kW Tower Load, h | 3 | 1.8333 | 1.8333 | 1.8333
| Tower run time on battery w/ 4kW Tower Load, h | 4 | 1.375 | 1.375 | 1.375
| Tower run time on battery w/ 5kW Tower Load, h | 5 | 1.1 | 1.1 | 1.1
| Tower run time on battery w/ 6kW Tower Load, h | 6 | 0.91667 | 0.91667 | 0.91667
Tcycle | Cycle time w/ 0kW Tower Load, h
| Cycle time w/ 0.5kW Tower Load, h |  | 12.1401 | 11.7152 | 11.8669
| Cycle time w/ 1kW Tower Load, h |  | 6.7797 | 6.2677 | 6.4453
| Cycle time w/ 2kW Tower Load, h |  | 4.4448 | 3.65 | 3.9041
| Cycle time w/ 3kW Tower Load, h |  | 4.3418 | 2.9205 | 3.3146
| Cycle time w/ 4kW Tower Load, h |  | 6.1999 | 2.7479 | 3.4423
| Cycle time w/ 5kW Tower Load, h |  | 64.1038 | 2.9622 | 4.5208
| Cycle time w/ 6kW Tower Load, h |  | -4.7808 | 3.81 | 10.8231
Engine duty cycle w/ 0kW Tower Load, %
| Engine duty cycle w/ 0.5kW Tower Load, % |  | 0.093912 | 0.061047 | 0.07305
| Engine duty cycle w/ 1kW Tower Load, % |  | 0.18876 | 0.12249 | 0.14666
| Engine duty cycle w/ 2kW Tower Load, % |  | 0.3813 | 0.24657 | 0.29561
| Engine duty cycle w/ 3kW Tower Load, % |  | 0.57775 | 0.37226 | 0.44689
| Engine duty cycle w/ 4kW Tower Load, % |  | 0.77822 | 0.49961 | 0.60056
| Engine duty cycle w/ 5kW Tower Load, % |  | 0.98284 | 0.62865 | 0.75668
| Engine duty cycle w/ 6kW Tower Load, % |  | Error | 0.75941 | 0.9153
| Engine life in years w/ 0kW Tower Load, y | 0
| Engine life in years w/ 0.5kW Tower Load, y | 0.5 | 18.2334 | 28.0493 | 23.4406
| Engine life in years w/ 1kW Tower Load, y | 1 | 9.0716 | 13.9796 | 11.6753
| Engine life in years w/ 2kW Tower Load, y | 2 | 4.4907 | 6.9447 | 5.7926
| Engine life in years w/ 3kW Tower Load, y | 3 | 2.9638 | 4.5998 | 3.8317
| Engine life in years w/ 4kW Tower Load, y | 4 | 2.2003 | 3.4273 | 2.8512
| Engine life in years w/ 5kW Tower Load, y | 5 | 1.7422 | 2.7238 | 2.263
| Engine life in years w/ 6kW Tower Load, y | 6 | Error | 2.2548 | 1.8708
| Battery life in years w/ 0kW Tower Load, y | 0
| Battery life in years w/ 0.5kW Tower Load, y | 0.5 | 10.3939 | 10.0301 | 10.16
| Battery life in years w/ 1kW Tower Load, y | 1 | 5.8046 | 5.3662 | 5.5182
| Battery life in years w/ 2kW Tower Load, y | 2 | 3.8055 | 3.125 | 3.3425
| Battery life in years w/ 3kW Tower Load, y | 3 | 3.7173 | 2.5005 | 2.8378
| Battery life in years w/ 4kW Tower Load, y | 4 | 5.3081 | 2.3526 | 2.9472
| Battery life in years w/ 5kW Tower Load, y | 5 | 54.8834 | 2.5361 | 3.8705
| Battery life in years w/ 6kW Tower Load, y | 6 | Error | 3.262 | 9.2664
| Engine maintenance interval w/ 0kW T.L., d | 0
| Engine maintenance interval w/ 0.5kW T.L., d | 0.5 | 443.6782 | 682.5322 | 570.389
| Engine maintenance interval w/ 1kW T.L., d | 1 | 220.7426 | 340.1696 | 284.098
| Engine maintenance interval w/ 2kW T.L., d | 2 | 109.2748 | 168.9883 | 140.9525
| Engine maintenance interval w/ 3kW T.L., d | 3 | 72.1189 | 111.9279 | 93.2373
| Engine maintenance interval w/ 4kW T.L., d | 4 | 53.5409 | 83.3977 | 69.3798
| Engine maintenance interval w/ 5kW T.L., d | 5 | 42.3941 | 66.2795 | 55.0652
| Engine maintenance interval w/ 6kW T.L., d | 6 | Error | 54.8674 | 45.5222