## Beckett Battery Modules
Boston Swing 5300 |  |  |  | Beckett 8224S Module |  |  |  | Approx |  | Stack of Beckett modules |  |  |  | Approx
| Nominal Capacity | 5.3 | Ah |  | Format Series | 7 | series |  |  |  | Format Series Stack | 11
| Nominal Energy | 19.3 | Wh |  | Format Parallel | 7 | parallel |  |  |  | Format Parallel Stack | 1
| Nominal Voltage | 3.65 | V |  | Nominal Capacity Module | 42.4 | Ah
| Max charge rate | 10.6 | A |  | Nominal Energy Module | 1100 | Wh
| Max discharge rate | 13 | A
| Voltage at 0% | 3.2 | V |  | Recommends 0.5C charge and 0.6C discharge
| Voltage at 30% | 3.4 | V
| Voltage at 80% | 3.85 | V
| Voltage at 100% | 4.2 | V |  | Voltage at 30% | 23.8 | V | 24V |  |  | Voltage at 30% | 261.8 | V | 260 | V | These are resting voltage numbers. When we're pushing
[5 empty] | Voltage at 80% | 26.95 | V | 27V |  |  | Voltage at 80% | 296.45 | V | 296 | V | charge into the stack, figure these numbers are going to be
around 10V higher.
[5 empty] | Checking module energy | 945.7 | Wh | 1kWh |  |  | Checking Stack Energy | 10402.7 | Wh | 10kWh
[5 empty] | Recommended charge 0.5C | 21.2 | A
[5 empty] | Recommended discharge 0.6C | 25 | A | 6950 | W
[5 empty] | Max discharge 1.2C | 50 | A
NovaTorque Alternator
| Rated load current | 24.4 | A
| Vac | 220 - 240 | Vac
| Vac peak 220 | 311.127 | Vac
| Vac peak 240 | 339.4113 | Vac
Looks like as the battery voltage comes up, the peaks of the sine waves
that make it through the rectifier get narrower. I bet this is the cause
of BK's observed drop of power into the battery.
This reminds me to look into the half wave / full wave rectifier question.

## Hygen Use Models
Info from Bill Kanz's 3 models of Hygen System Design, 3/1/2016.
| Beckett module nominal energy, kWh | 1 |  | Engine spec'd life, h | 20000
| Stack height | 11 |  | Hours in a year, h | 8760
| Batt bank energy, kWh | 11 |  | Engine service interval, h | 1000
| Batt end of life definition, capacity degradation | 80%
| Avg bank energy over lifetime | 90%
| Depth of Discharge, % | 50%
| Cycle energy, kWh | 4.95 |  | SFC, l/kWh | 0.38
| Batt Cycles 80% DOD | 3000 |  | Fuel Tank Capacity, l | 1000
| Batt Cycles 50% DOD, 0.5C charge, estimated by Boston Power | 10000 |  | Diesel cost, $/l | 1
| Bill Kanz's analysis: |  | 2 cylinder | 3 cylinder | 3 cylinder
|  |  |  | Limited by Engine Load Factor | Limited by Today's NovaTorque
A | Engine gross intermittent power, kW |  | 10.3 | 15.3 | 15.3
| Maximum engine load factor, % |  | 70% | 70% | 59%
B | Engine net intermittent power, kW |  | 7.21 | 10.71 | 9.027
| Engine efficiency (after fan, alternator, etc.), % |  | 88% | 88% | 88%
C | Engine max net weighted power, kW |  | 6.3448 | 9.4248 | 7.9438
| Alternator power efficiency, % |  | 94% | 94% | 94%
D | Alternator max output (calculated), kW |  | 5.9641 | 8.8593 | 7.4671
D | NovaTorque max power, kW |  | 7.5 | 8.8593 | 7.5
| Rectifier power efficiency, % |  | 99% | 99% | 99%
E1 | Rectifier max output, kW |  | 5.9045 | 8.7707 | 7.425
| DC - DC converter power efficiency, % |  | 95% | 95% | 95%
F1 | Max rated DC power output, kW |  | 5.6092 | 8.3322 | 7.0537
F4 | Spec'd AC max accessory load, kW |  | 0.5 | 0.5 | 0.5
| Estimated AC inverter efficiency, % |  | 95% | 95% | 95%
F3 | AC accessory load, kW |  | 0.52632 | 0.52632 | 0.52632
F2 | Max rated tower load, kW |  | 5.0829 | 7.8059 | 6.5274
[6 empty] | Tower Load, kW | Fuel Cost per Month, $USD | 1000 liter tank refill interval, days | 250 liter tank refill interval, d | Engine maintenance interval, days
| Bill Marty's analysis: |  |  |  |  | 0 | 0
| Working back upstream from tower load to battery charging. | Tower Load, kW |  |  |  | 0.5 | 139.08 | 219.2982 | 54.8246 | 570.389
E3 | Power available to charge battery bank, kW | 0 | 5.3505 | 8.2167 | 6.871 | 1 | 278.16 | 109.6491 | 27.4123 | 284.098
| Power available to charge battery bank, kW | 0.5 | 4.8241 | 7.6904 | 6.3447 | 2 | 556.32 | 54.8246 | 13.7061 | 140.9525
| Power available to charge battery bank, kW | 1 | 4.2978 | 7.1641 | 5.8184 | 3 | 834.48 | 36.5497 | 9.1374 | 93.2373
| Power available to charge battery bank, kW | 2 | 3.2452 | 6.1114 | 4.7657 | 4 | 1112.64 | 27.4123 | 6.8531 | 69.3798
| Power available to charge battery bank, kW | 3 | 2.1926 | 5.0588 | 3.7131 | 5 | 1390.8 | 21.9298 | 5.4825 | 55.0652
| Power available to charge battery bank, kW | 4 | 1.1399 | 4.0062 | 2.6605 | 6 | 1668.96 | 18.2749 | 4.5687 | 45.5222
| Power available to charge battery bank, kW | 5 | 0.087296 | 2.9535 | 1.6078
| Power available to charge battery bank, kW | 6 | -0.96534 | 1.9009 | 0.55519
| Battery C-rate w/ 0kW Tower Load |  | 0.54045 | 0.82997 | 0.69404
| Battery C-rate w/ 0.5kW Tower Load |  | 0.48729 | 0.77681 | 0.64088
| Battery C-rate w/ 1kW Tower Load |  | 0.43412 | 0.72364 | 0.58771
| Battery C-rate w/ 2kW Tower Load |  | 0.3278 | 0.61732 | 0.48139
| Battery C-rate w/ 3kW Tower Load |  | 0.22147 | 0.51099 | 0.37506
| Battery C-rate w/ 4kW Tower Load |  | 0.11514 | 0.40466 | 0.26873
| Battery C-rate w/ 5kW Tower Load |  | 0.0088178 | 0.29834 | 0.16241
| Battery C-rate w/ 6kW Tower Load |  | -0.097509 | 0.19201 | 0.05608
Tcharge | Engine on time to charge battery w/ 0kW Tower Load, h |  | 0.92516 | 0.60243 | 0.72042
| Engine on time to charge battery w/ 0.5kW Tower Load, h |  | 1.0261 | 0.64366 | 0.78018
| Engine on time to charge battery w/ 1kW Tower Load, h |  | 1.1517 | 0.69095 | 0.85076
| Engine on time to charge battery w/ 2kW Tower Load, h |  | 1.5253 | 0.80996 | 1.0387
| Engine on time to charge battery w/ 3kW Tower Load, h |  | 2.2576 | 0.97849 | 1.3331
| Engine on time to charge battery w/ 4kW Tower Load, h |  | 4.3424 | 1.2356 | 1.8606
| Engine on time to charge battery w/ 5kW Tower Load, h |  | 56.7034 | 1.676 | 3.0787 | [5 empty] | These plots customized for Angus's Chilean customer.
| Engine on time to charge battery w/ 6kW Tower Load, h |  | -5.1278 | 2.604 | 8.9158
Tdischarge | Tower run time on battery w/ 0kW Tower Load, h | 0
| Tower run time on battery w/ 0.5kW Tower Load, h | 0.5 | 9.9 | 9.9 | 9.9
| Tower run time on battery w/ 1kW Tower Load, h | 1 | 4.95 | 4.95 | 4.95
| Tower run time on battery w/ 2kW Tower Load, h | 2 | 2.475 | 2.475 | 2.475
| Tower run time on battery w/ 3kW Tower Load, h | 3 | 1.65 | 1.65 | 1.65
| Tower run time on battery w/ 4kW Tower Load, h | 4 | 1.2375 | 1.2375 | 1.2375
| Tower run time on battery w/ 5kW Tower Load, h | 5 | 0.99 | 0.99 | 0.99
| Tower run time on battery w/ 6kW Tower Load, h | 6 | 0.825 | 0.825 | 0.825
Tcycle | Cycle time w/ 0kW Tower Load, h
| Cycle time w/ 0.5kW Tower Load, h |  | 10.9261 | 10.5437 | 10.6802
| Cycle time w/ 1kW Tower Load, h |  | 6.1017 | 5.6409 | 5.8008
| Cycle time w/ 2kW Tower Load, h |  | 4.0003 | 3.285 | 3.5137
| Cycle time w/ 3kW Tower Load, h |  | 3.9076 | 2.6285 | 2.9831
| Cycle time w/ 4kW Tower Load, h |  | 5.5799 | 2.4731 | 3.0981
| Cycle time w/ 5kW Tower Load, h |  | 57.6934 | 2.666 | 4.0687
| Cycle time w/ 6kW Tower Load, h |  | -4.3028 | 3.429 | 9.7408
Engine duty cycle w/ 0kW Tower Load, %
| Engine duty cycle w/ 0.5kW Tower Load, % |  | 0.093912 | 0.061047 | 0.07305
| Engine duty cycle w/ 1kW Tower Load, % |  | 0.18876 | 0.12249 | 0.14666
| Engine duty cycle w/ 2kW Tower Load, % |  | 0.3813 | 0.24657 | 0.29561
| Engine duty cycle w/ 3kW Tower Load, % |  | 0.57775 | 0.37226 | 0.44689
| Engine duty cycle w/ 4kW Tower Load, % |  | 0.77822 | 0.49961 | 0.60056
| Engine duty cycle w/ 5kW Tower Load, % |  | 0.98284 | 0.62865 | 0.75668
| Engine duty cycle w/ 6kW Tower Load, % |  | Error | 0.75941 | 0.9153
| Engine life in years w/ 0kW Tower Load, y | 0
| Engine life in years w/ 0.5kW Tower Load, y | 0.5 | 24.3111 | 37.399 | 31.2542
| Engine life in years w/ 1kW Tower Load, y | 1 | 12.0955 | 18.6394 | 15.567
| Engine life in years w/ 2kW Tower Load, y | 2 | 5.9877 | 9.2596 | 7.7234
| Engine life in years w/ 3kW Tower Load, y | 3 | 3.9517 | 6.133 | 5.1089
| Engine life in years w/ 4kW Tower Load, y | 4 | 2.9337 | 4.5697 | 3.8016
| Engine life in years w/ 5kW Tower Load, y | 5 | 2.323 | 3.6318 | 3.0173
| Engine life in years w/ 6kW Tower Load, y | 6 | Error | 3.0064 | 2.4944
| Battery life in years w/ 0kW Tower Load, y | 0
| Battery life in years w/ 0.5kW Tower Load, y | 0.5 | 12.4727 | 12.0361 | 12.192
| Battery life in years w/ 1kW Tower Load, y | 1 | 6.9655 | 6.4394 | 6.6219
| Battery life in years w/ 2kW Tower Load, y | 2 | 4.5666 | 3.75 | 4.011
| Battery life in years w/ 3kW Tower Load, y | 3 | 4.4608 | 3.0006 | 3.4054
| Battery life in years w/ 4kW Tower Load, y | 4 | 6.3697 | 2.8232 | 3.5366
| Battery life in years w/ 5kW Tower Load, y | 5 | 65.86 | 3.0433 | 4.6446
| Battery life in years w/ 6kW Tower Load, y | 6 | Error | 3.9144 | 11.1196
| Engine maintenance interval w/ 0kW T.L., d | 0
| Engine maintenance interval w/ 0.5kW T.L., d | 0.5 | 443.6782 | 682.5322 | 570.389
| Engine maintenance interval w/ 1kW T.L., d | 1 | 220.7426 | 340.1696 | 284.098
| Engine maintenance interval w/ 2kW T.L., d | 2 | 109.2748 | 168.9883 | 140.9525
| Engine maintenance interval w/ 3kW T.L., d | 3 | 72.1189 | 111.9279 | 93.2373
| Engine maintenance interval w/ 4kW T.L., d | 4 | 53.5409 | 83.3977 | 69.3798
| Engine maintenance interval w/ 5kW T.L., d | 5 | 42.3941 | 66.2795 | 55.0652
| Engine maintenance interval w/ 6kW T.L., d | 6 | Error | 54.8674 | 45.5222

## 5 year life projections
Info from Bill Kanz's 3 models of Hygen System Design, 3/1/2016.
| Battery Parameters |  |  | Battery Parameters |  |  | 4 sets of assumptions
| Beckett module nominal energy, kWh | 1 |  | Beckett module nominal energy, kWh | 1 | 1 | 1 | 1.1
| Stack height | 11 |  | Stack height | 11 | 11 | 11 | 11
| Batt bank energy, kWh | 11 |  | Batt bank energy, kWh | 11 | 11 | 11 | 12.1
| Batt end of life definition, capacity degradation | 80% |  | Batt end of life definition, capacity degradation | 80% | 80% | 80% | 70%
| Avg bank energy over lifetime | 90% |  | Avg bank energy over lifetime | 90% | 90% | 90% | 85%
| Depth of Discharge, % | 50% |  | Depth of Discharge, % | 50% | 50% | 50% | 50%
| Cycle energy, kWh | 4.95 |  | Cycle energy, kWh | 4.95 | 4.95 | 4.95 | 5.1425
| Batt Cycles 80% DOD | 3000 |  | Batt Cycles 80% DOD | 3000 | 3000 | 3000 | 3000
| Batt Cycles 50% DOD, 0.5C charge, estimated by Boston Power | 10000 |  | Batt Cycles 50% DOD, 0.5C charge, estimated by Boston Power | 7500 | 7500 | 10000 | 10000
| Batt Cycles, projected based on end of life extension |  |  | Batt Cycles, projected based on end of life extension | 3000 | 7500 | 10000 | 15000
| Engine Parameters |  |  | Engine Parameters
| Engine spec'd life, h | 20000 |  | Engine spec'd life, h | 15000 | 15000 | 20000 | 25000
| Hours in a year, h | 8760 |  | Hours in a year, h | 8760 | 8760 | 8760 | 8760
| Engine service interval, h | 1000 |  | Engine service interval, h | 1000 | 1000 | 1000 | 1000
| SFC, l/kWh | 0.38 |  | SFC, l/kWh | 0.38 | 0.38 | 0.38 | 0.38
| Fuel Tank Capacity, l | 1000 |  | Fuel Tank Capacity, l | 1000 | 1000 | 1000 | 1000
| Diesel cost, $/l | 1 |  | Diesel cost, $/l | 1 | 1 | 1 | 1
| Bill Kanz's analysis: |  | 3 cylinder
Limited by Today's NovaTorque
A | Engine gross intermittent power, kW |  | 15.3
| Maximum engine load factor, % |  | 59%
B | Engine net intermittent power, kW |  | 9.027
| Engine efficiency (after fan, alternator, etc.), % |  | 88%
C | Engine max net weighted power, kW |  | 7.9438
| Alternator power efficiency, % |  | 94%
D | Alternator max output (calculated), kW |  | 7.4671
D | NovaTorque max power, kW |  | 7.5
| Rectifier power efficiency, % |  | 99%
E1 | Rectifier max output, kW |  | 7.425
| DC - DC converter power efficiency, % |  | 95%
F1 | Max rated DC power output, kW |  | 7.0537
F4 | Spec'd AC max accessory load, kW |  | 0
| Estimated AC inverter efficiency, % |  | 95%
F3 | AC accessory load, kW |  | 0
F2 | Max rated tower load, kW |  | 7.0537
[9 empty] | Tower Load, kW | Fuel Cost per Month, $USD | 1000 liter tank refill interval, days | 250 liter tank refill interval, d | Engine maintenance interval, days
| Bill Marty's analysis: |  |  |  | Beckett battery spec | Life under most conservative assumptions | Middle case | Life under most optimistic assumptions | 0 | 0
| Working back upstream from tower load to battery charging. | Tower Load, kW | [6 empty] | 0.5 | 139.08 | 219.2982 | 54.8246 | 616.557
E3 | Power available to charge battery bank, kW | 0 | 7.425 |  | 7.425 | 7.425 | 7.425 | 7.425 | 1 | 278.16 | 109.6491 | 27.4123 | 307.182
| Power available to charge battery bank, kW | 0.5 | 6.8987 |  | 6.8987 | 6.8987 | 6.8987 | 6.8987 | 2 | 556.32 | 54.8246 | 13.7061 | 152.4945
| Power available to charge battery bank, kW | 1 | 6.3724 |  | 6.3724 | 6.3724 | 6.3724 | 6.3724 | 3 | 834.48 | 36.5497 | 9.1374 | 100.932
| Power available to charge battery bank, kW | 2 | 5.3197 |  | 5.3197 | 5.3197 | 5.3197 | 5.3197 | 4 | 1112.64 | 27.4123 | 6.8531 | 75.1508
| Power available to charge battery bank, kW | 3 | 4.2671 |  | 4.2671 | 4.2671 | 4.2671 | 4.2671 | 5 | 1390.8 | 21.9298 | 5.4825 | 59.682
| Power available to charge battery bank, kW | 4 | 3.2145 |  | 3.2145 | 3.2145 | 3.2145 | 3.2145 | 6 | 1668.96 | 18.2749 | 4.5687 | 49.3695
| Power available to charge battery bank, kW | 5 | 2.1618 |  | 2.1618 | 2.1618 | 2.1618 | 2.1618
| Power available to charge battery bank, kW | 6 | 1.1092 |  | 1.1092 | 1.1092 | 1.1092 | 1.1092
| Battery C-rate w/ 0kW Tower Load |  | 0.75 |  | 0.75 | 0.75 | 0.75 | 0.72193
| Battery C-rate w/ 0.5kW Tower Load |  | 0.69684 |  | 0.69684 | 0.69684 | 0.69684 | 0.67075
| Battery C-rate w/ 1kW Tower Load |  | 0.64367 |  | 0.64367 | 0.64367 | 0.64367 | 0.61958
| Battery C-rate w/ 2kW Tower Load |  | 0.53735 |  | 0.53735 | 0.53735 | 0.53735 | 0.51723
| Battery C-rate w/ 3kW Tower Load |  | 0.43102 |  | 0.43102 | 0.43102 | 0.43102 | 0.41489
| Battery C-rate w/ 4kW Tower Load |  | 0.32469 |  | 0.32469 | 0.32469 | 0.32469 | 0.31254
| Battery C-rate w/ 5kW Tower Load |  | 0.21837 |  | 0.21837 | 0.21837 | 0.21837 | 0.21019
| Battery C-rate w/ 6kW Tower Load |  | 0.11204 |  | 0.11204 | 0.11204 | 0.11204 | 0.10785
Tcharge | Engine on time to charge battery w/ 0kW Tower Load, h |  | 0.66667 |  | 0.66667 | 0.66667 | 0.66667 | 0.69259
| Engine on time to charge battery w/ 0.5kW Tower Load, h |  | 0.71753 |  | 0.71753 | 0.71753 | 0.71753 | 0.74543
| Engine on time to charge battery w/ 1kW Tower Load, h |  | 0.77679 |  | 0.77679 | 0.77679 | 0.77679 | 0.807
| Engine on time to charge battery w/ 2kW Tower Load, h |  | 0.9305 |  | 0.9305 | 0.9305 | 0.9305 | 0.96668
| Engine on time to charge battery w/ 3kW Tower Load, h |  | 1.16 |  | 1.16 | 1.16 | 1.16 | 1.2051
| Engine on time to charge battery w/ 4kW Tower Load, h |  | 1.5399 |  | 1.5399 | 1.5399 | 1.5399 | 1.5998
| Engine on time to charge battery w/ 5kW Tower Load, h |  | 2.2897 |  | 2.2897 | 2.2897 | 2.2897 | 2.3788 | [5 empty] | These plots customized for Angus's Chilean customer.
| Engine on time to charge battery w/ 6kW Tower Load, h |  | 4.4626 |  | 4.4626 | 4.4626 | 4.4626 | 4.6362
Tdischarge | Tower run time on battery w/ 0kW Tower Load, h | 0
| Tower run time on battery w/ 0.5kW Tower Load, h | 0.5 | 9.9 |  | 9.9 | 9.9 | 9.9 | 10.285
| Tower run time on battery w/ 1kW Tower Load, h | 1 | 4.95 |  | 4.95 | 4.95 | 4.95 | 5.1425
| Tower run time on battery w/ 2kW Tower Load, h | 2 | 2.475 |  | 2.475 | 2.475 | 2.475 | 2.5713
| Tower run time on battery w/ 3kW Tower Load, h | 3 | 1.65 |  | 1.65 | 1.65 | 1.65 | 1.7142
| Tower run time on battery w/ 4kW Tower Load, h | 4 | 1.2375 |  | 1.2375 | 1.2375 | 1.2375 | 1.2856
| Tower run time on battery w/ 5kW Tower Load, h | 5 | 0.99 |  | 0.99 | 0.99 | 0.99 | 1.0285
| Tower run time on battery w/ 6kW Tower Load, h | 6 | 0.825 |  | 0.825 | 0.825 | 0.825 | 0.85708
Tcycle | Cycle time w/ 0kW Tower Load, h
| Cycle time w/ 0.5kW Tower Load, h |  | 10.6175 |  | 10.6175 | 10.6175 | 10.6175 | 11.0304
| Cycle time w/ 1kW Tower Load, h |  | 5.7268 |  | 5.7268 | 5.7268 | 5.7268 | 5.9495
| Cycle time w/ 2kW Tower Load, h |  | 3.4055 |  | 3.4055 | 3.4055 | 3.4055 | 3.5379
| Cycle time w/ 3kW Tower Load, h |  | 2.81 |  | 2.81 | 2.81 | 2.81 | 2.9193
| Cycle time w/ 4kW Tower Load, h |  | 2.7774 |  | 2.7774 | 2.7774 | 2.7774 | 2.8854
| Cycle time w/ 5kW Tower Load, h |  | 3.2797 |  | 3.2797 | 3.2797 | 3.2797 | 3.4073
| Cycle time w/ 6kW Tower Load, h |  | 5.2876 |  | 5.2876 | 5.2876 | 5.2876 | 5.4933
Engine duty cycle w/ 0kW Tower Load, %
| Engine duty cycle w/ 0.5kW Tower Load, % |  | 0.06758 |  | 0.06758 | 0.06758 | 0.06758 | 0.06758
| Engine duty cycle w/ 1kW Tower Load, % |  | 0.13564 |  | 0.13564 | 0.13564 | 0.13564 | 0.13564
| Engine duty cycle w/ 2kW Tower Load, % |  | 0.27323 |  | 0.27323 | 0.27323 | 0.27323 | 0.27323
| Engine duty cycle w/ 3kW Tower Load, % |  | 0.41282 |  | 0.41282 | 0.41282 | 0.41282 | 0.41282
| Engine duty cycle w/ 4kW Tower Load, % |  | 0.55444 |  | 0.55444 | 0.55444 | 0.55444 | 0.55444
| Engine duty cycle w/ 5kW Tower Load, % |  | 0.69814 |  | 0.69814 | 0.69814 | 0.69814 | 0.69814
| Engine duty cycle w/ 6kW Tower Load, % |  | 0.84398 |  | 0.84398 | 0.84398 | 0.84398 | 0.84398
| Engine life in years w/ 0kW Tower Load, y | 0
| Engine life in years w/ 0.5kW Tower Load, y | 0.5 | 33.7839 |  | 25.338 | 25.338 | 33.7839 | 42.2299
| Engine life in years w/ 1kW Tower Load, y | 1 | 16.8319 |  | 12.6239 | 12.6239 | 16.8319 | 21.0399
| Engine life in years w/ 2kW Tower Load, y | 2 | 8.3559 |  | 6.2669 | 6.2669 | 8.3559 | 10.4448
| Engine life in years w/ 3kW Tower Load, y | 3 | 5.5305 |  | 4.1479 | 4.1479 | 5.5305 | 6.9132
| Engine life in years w/ 4kW Tower Load, y | 4 | 4.1179 |  | 3.0884 | 3.0884 | 4.1179 | 5.1473
| Engine life in years w/ 5kW Tower Load, y | 5 | 3.2702 |  | 2.4527 | 2.4527 | 3.2702 | 4.0878
| Engine life in years w/ 6kW Tower Load, y | 6 | 2.7052 |  | 2.0289 | 2.0289 | 2.7052 | 3.3815
| Battery life in years w/ 0kW Tower Load, y | 0
| Battery life in years w/ 0.5kW Tower Load, y | 0.5 | 12.1205 |  | 3.6361 | 9.0903 | 12.1205 | 18.8877
| Battery life in years w/ 1kW Tower Load, y | 1 | 6.5374 |  | 1.9612 | 4.9031 | 6.5374 | 10.1875
| Battery life in years w/ 2kW Tower Load, y | 2 | 3.8876 |  | 1.1663 | 2.9157 | 3.8876 | 6.0581
| Battery life in years w/ 3kW Tower Load, y | 3 | 3.2078 |  | 0.96234 | 2.4059 | 3.2078 | 4.9988
| Battery life in years w/ 4kW Tower Load, y | 4 | 3.1706 |  | 0.95117 | 2.3779 | 3.1706 | 4.9408
| Battery life in years w/ 5kW Tower Load, y | 5 | 3.744 |  | 1.1232 | 2.808 | 3.744 | 5.8343
| Battery life in years w/ 6kW Tower Load, y | 6 | 6.0361 |  | 1.8108 | 4.5271 | 6.0361 | 9.4063
| Engine maintenance interval w/ 0kW T.L., d | 0
| Engine maintenance interval w/ 0.5kW T.L., d | 0.5 | 616.557 |  | 616.557 | 616.557 | 616.557 | 616.557
| Engine maintenance interval w/ 1kW T.L., d | 1 | 307.182 |  | 307.182 | 307.182 | 307.182 | 307.182
| Engine maintenance interval w/ 2kW T.L., d | 2 | 152.4945 |  | 152.4945 | 152.4945 | 152.4945 | 152.4945
| Engine maintenance interval w/ 3kW T.L., d | 3 | 100.932 |  | 100.932 | 100.932 | 100.932 | 100.932
| Engine maintenance interval w/ 4kW T.L., d | 4 | 75.1508 |  | 75.1508 | 75.1508 | 75.1508 | 75.1508
| Engine maintenance interval w/ 5kW T.L., d | 5 | 59.682 |  | 59.682 | 59.682 | 59.682 | 59.682
| Engine maintenance interval w/ 6kW T.L., d | 6 | 49.3695 |  | 49.3695 | 49.3695 | 49.3695 | 49.3695